	Electrical Isolation Permit
Hollins & Reed Contracting Ltd



	Permit no.
HR-0423
	Site
Unit 3, Canal Side Business Park
	Exact location
Plant room, board DB-2



	Details
	
	
	
	
	

	Contractor
	Hollins & Reed
	Issued to
	Callum Whittle
	Valid from
	26/10/26 08:00

	Valid to
	26/10/26 16:30
	RAMS ref
	HR-RAMS-13
	Isolation cert
	ISO-0423



	The work
	

	Equipment or circuit
	Sub-main board DB-2, fed by main switchboard ways 4 and 6, with a generator inlet.

	Work to be done
	Replace DB-2, re-terminate its circuits. No live work. Any change needs a new permit.



	Circuit isolated
	Point of isolation
	Lock no.
	Tag
	Proved dead by
	Test instrument

	Incomer A, general
	Main switchboard way 4
	L1
	T1
	Glen Aspinall
	Tester V1, unit P1

	Incomer B, Tanyard Air
	Main switchboard way 6
	L2
	T2
	Glen Aspinall
	Tester V1, unit P1

	Generator inlet
	Inlet isolator beside DB-2
	L3
	T3
	Glen Aspinall
	Tester V1, unit P1



	Precautions
	Done
	By

	Isolated at the source
	☒
	Glen Aspinall

	Locked and tagged
	☒
	Glen Aspinall, box B1

	Fuses or links held safe
	☐
	Not needed. Breakers

	Proved dead at the work, tester proved
	☒
	Glen Aspinall

	Earthed where needed
	☐
	Not needed. See below

	Equipment marked, danger notices up
	☒
	Callum Whittle

	Adjacent live parts screened
	☒
	Callum Whittle

	Key held by
	☒
	Whittle, Tunnicliffe



	Hazards
	
	
	
	
	
	
	

	Live parts nearby
	☒
	Stored energy
	☐
	Back-feed
	☒
	Generator, inverter
	☐

	Capacitors
	☐
	
	☐
	
	☐
	
	☐



	People on this permit: name
	Company
	Briefed

	Callum Whittle
	Hollins & Reed
	☒

	Kieran Tunnicliffe
	Tanyard Air
	☒



	Other conditions

	Before issue: 07:10 ways 4, 6 and inlet isolator off. 07:15 L1 to L3 on, keys in lock-out box B1, Whittle and Tunnicliffe each lock it, keep their key. 07:18 tags on. 07:25 tester proved on P1. 07:30 DB-2 proved dead, every way and conductor, no back-feed at inlet. 07:50 tester proved again. 07:52 screen, danger notice up at main switchboard. 07:55 issued.

	Main switchboard stays live. No earths: low voltage, inlet locked, no generator on site.



	Sign-off
	Name
	Signature
	Date
	Time

	Issued: precautions checked
	Glen Aspinall
	signed
	26/10/26
	07:55

	Accepted: permit understood
	Callum Whittle
	signed
	26/10/26
	07:58
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	Cancellation
	

	Work complete
	15:40. New DB-2 fitted and re-terminated. BS 7671 dead tests done, results on the certificate.

	Tools and earths removed
	Cleared by Callum Whittle: tools out, covers on. No earths were fitted.

	People clear
	Callum Whittle and Kieran Tunnicliffe told the board is going live, 15:48.



	Handback
	

	Locks removed by
	Callum Whittle and Kieran Tunnicliffe took their locks off box B1 at 15:50. Glen Aspinall took off L1 to L3 at 15:55. Tags and notices off.

	Re-energised at
	16:00 way 4, 16:05 way 6, by Glen Aspinall.

	Tested by
	Callum Whittle: live tests after energising passed. Fans run, checked by Kieran Tunnicliffe.

	Notes
	Certificate EIC-0423 in the job file. Screen at the main switchboard down at 16:15.

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	



	Sign-off
	Name
	Signature
	Date
	Time

	Extended: new end time
	Not extended
	
	
	

	Cancelled: area checked
	Glen Aspinall
	signed
	26/10/26
	15:48

	Handed back: area returned
	Glen Aspinall
	signed
	26/10/26
	16:20



Worked example of a made-up job. Not a permit.   ·   Page 1 of 1
