Electrical Isolation Permit Hollins & Reed Contracting Ltd

| Permit no. HR-0423 | Site Unit 3, Canal Side Business Park | Exact location Plant room, board DB-2 |
| --- | --- | --- |

| Details |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contractor | Hollins & Reed | Issued to | Callum Whittle | Valid from | 26/10/26 08:00 |
| Valid to | 26/10/26 16:30 | RAMS ref | HR-RAMS-13 | Isolation cert | ISO-0423 |

| The work |  |
| --- | --- |
| Equipment or circuit | Sub-main board DB-2, fed by main switchboard ways 4 and 6, with a generator inlet. |
| Work to be done | Replace DB-2, re-terminate its circuits. No live work. Any change needs a new permit. |

| Circuit isolated | Point of isolation | Lock no. | Tag | Proved dead by | Test instrument |
| --- | --- | --- | --- | --- | --- |
| Incomer A, general | Main switchboard way 4 | L1 | T1 | Glen Aspinall | Tester V1, unit P1 |
| Incomer B, Tanyard Air | Main switchboard way 6 | L2 | T2 | Glen Aspinall | Tester V1, unit P1 |
| Generator inlet | Inlet isolator beside DB-2 | L3 | T3 | Glen Aspinall | Tester V1, unit P1 |

| Precautions | Done | By |
| --- | --- | --- |
| Isolated at the source | ☒ | Glen Aspinall |
| Locked and tagged | ☒ | Glen Aspinall, box B1 |
| Fuses or links held safe | ☐ | Not needed. Breakers |
| Proved dead at the work, tester proved | ☒ | Glen Aspinall |
| Earthed where needed | ☐ | Not needed. See below |
| Equipment marked, danger notices up | ☒ | Callum Whittle |
| Adjacent live parts screened | ☒ | Callum Whittle |
| Key held by | ☒ | Whittle, Tunnicliffe |

| Hazards |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Live parts nearby | ☒ | Stored energy | ☐ | Back-feed | ☒ | Generator, inverter | ☐ |
| Capacitors | ☐ |  | ☐ |  | ☐ |  | ☐ |

| People on this permit: name | Company | Briefed |
| --- | --- | --- |
| Callum Whittle | Hollins & Reed | ☒ |
| Kieran Tunnicliffe | Tanyard Air | ☒ |

Other conditions

Before issue: 07:10 ways 4, 6 and inlet isolator off. 07:15 L1 to L3 on, keys in lock-out box B1, Whittle and Tunnicliffe each lock it, keep their key. 07:18 tags on. 07:25 tester proved on P1. 07:30 DB-2 proved dead, every way and conductor, no back-feed at inlet. 07:50 tester proved again. 07:52 screen, danger notice up at main switchboard. 07:55 issued.

Main switchboard stays live. No earths: low voltage, inlet locked, no generator on site.

| Sign-off | Name | Signature | Date | Time |
| --- | --- | --- | --- | --- |
| Issued: precautions checked | Glen Aspinall | signed | 26/10/26 | 07:55 |
| Accepted: permit understood | Callum Whittle | signed | 26/10/26 | 07:58 |

Electrical Isolation Permit Hollins & Reed Contracting Ltd

| Permit no. HR-0423 | Site Unit 3, Canal Side Business Park | Exact location Plant room, board DB-2 |
| --- | --- | --- |

| Cancellation |  |
| --- | --- |
| Work complete | 15:40. New DB-2 fitted and re-terminated. BS 7671 dead tests done, results on the certificate. |
| Tools and earths removed | Cleared by Callum Whittle: tools out, covers on. No earths were fitted. |
| People clear | Callum Whittle and Kieran Tunnicliffe told the board is going live, 15:48. |

| Handback |  |
| --- | --- |
| Locks removed by | Callum Whittle and Kieran Tunnicliffe took their locks off box B1 at 15:50. Glen Aspinall took off L1 to L3 at 15:55. Tags and notices off. |
| Re-energised at | 16:00 way 4, 16:05 way 6, by Glen Aspinall. |
| Tested by | Callum Whittle: live tests after energising passed. Fans run, checked by Kieran Tunnicliffe. |
| Notes | Certificate EIC-0423 in the job file. Screen at the main switchboard down at 16:15. |

| Sign-off | Name | Signature | Date | Time |
| --- | --- | --- | --- | --- |
| Extended: new end time | Not extended |  |  |  |
| Cancelled: area checked | Glen Aspinall | signed | 26/10/26 | 15:48 |
| Handed back: area returned | Glen Aspinall | signed | 26/10/26 | 16:20 |