## Electrical Isolation Permit
Electrical Isolation Permit
Hollins & Reed Contracting Ltd
Permit no. |  | Site | [10 empty] | Exact location
HR-0423 |  | Unit 3, Canal Side Business Park | [10 empty] | Plant room, board DB-2
Details
Contractor | Hollins & Reed |  |  |  |  | Issued to |  |  |  | Callum Whittle |  |  |  |  | Valid from |  |  |  |  | 26/10/26 08:00
Valid to | 26/10/26 16:30 |  |  |  |  | RAMS ref |  |  |  | HR-RAMS-13 |  |  |  |  | Isolation cert |  |  |  |  | ISO-0423
The work
Equipment or circuit |  |  |  | Sub-main board DB-2, fed by main switchboard ways 4 and 6, with a generator inlet.
Work to be done |  |  |  | Replace DB-2, re-terminate its circuits. No live work. Any change needs a new permit.
Circuit isolated |  |  | Point of isolation |  |  |  |  | Lock no. |  |  |  |  | Tag | Proved dead by | [5 empty] | Test instrument
Incomer A, general |  |  | Main switchboard way 4 |  |  |  |  | L1 |  |  |  |  | T1 | Glen Aspinall | [5 empty] | Tester V1, unit P1
Incomer B, Tanyard Air |  |  | Main switchboard way 6 |  |  |  |  | L2 |  |  |  |  | T2 | Glen Aspinall | [5 empty] | Tester V1, unit P1
Generator inlet |  |  | Inlet isolator beside DB-2 |  |  |  |  | L3 |  |  |  |  | T3 | Glen Aspinall | [5 empty] | Tester V1, unit P1
Precautions | [13 empty] | Done |  |  |  | By
Isolated at the source | [13 empty] | ☒ |  |  |  | Glen Aspinall
Locked and tagged | [13 empty] | ☒ |  |  |  | Glen Aspinall, box B1
Fuses or links held safe | [13 empty] | ☐ |  |  |  | Not needed. Breakers
Proved dead at the work, tester proved | [13 empty] | ☒ |  |  |  | Glen Aspinall
Earthed where needed | [13 empty] | ☐ |  |  |  | Not needed. See below
Equipment marked, danger notices up | [13 empty] | ☒ |  |  |  | Callum Whittle
Adjacent live parts screened | [13 empty] | ☒ |  |  |  | Callum Whittle
Key held by | [13 empty] | ☒ |  |  |  | Whittle, Tunnicliffe
Hazards
Live parts nearby |  | ☒ |  | Stored energy |  |  | ☐ |  |  |  | Back-feed |  |  |  |  | ☒ | Generator, inverter | [5 empty] | ☐
Capacitors |  | ☐ |  |  |  |  | ☐ | [8 empty] | ☐ | [6 empty] | ☐
People on this permit: name | [8 empty] | Company | [11 empty] | Briefed
Callum Whittle | [8 empty] | Hollins & Reed | [11 empty] | ☒
Kieran Tunnicliffe | [8 empty] | Tanyard Air | [11 empty] | ☒
Other conditions
Before issue: 07:10 ways 4, 6 and inlet isolator off. 07:15 L1 to L3 on, keys in lock-out box B1, Whittle and Tunnicliffe each lock it, keep their key. 07:18 tags on. 07:25 tester proved on P1. 07:30 DB-2 proved dead, every way and conductor, no back-feed at inlet. 07:50 tester proved again. 07:52 screen, danger notice up at main switchboard. 07:55 issued.
Main switchboard stays live. No earths: low voltage, inlet locked, no generator on site.
Sign-off |  |  |  |  | Name | [6 empty] | Signature | [6 empty] | Date |  |  | Time
Issued: precautions checked |  |  |  |  | Glen Aspinall | [6 empty] | signed | [6 empty] | 26/10/26 |  |  | 07:55
Accepted: permit understood |  |  |  |  | Callum Whittle | [6 empty] | signed | [6 empty] | 26/10/26 |  |  | 07:58
Worked example of a made-up job. Not a permit. · Page 1 of 2
Electrical Isolation Permit
Hollins & Reed Contracting Ltd
Permit no. |  | Site | [10 empty] | Exact location
HR-0423 |  | Unit 3, Canal Side Business Park | [10 empty] | Plant room, board DB-2
Cancellation
Work complete |  |  |  | 15:40. New DB-2 fitted and re-terminated. BS 7671 dead tests done, results on the certificate.
Tools and earths removed |  |  |  | Cleared by Callum Whittle: tools out, covers on. No earths were fitted.
People clear |  |  |  | Callum Whittle and Kieran Tunnicliffe told the board is going live, 15:48.
Handback
Locks removed by |  |  |  | Callum Whittle and Kieran Tunnicliffe took their locks off box B1 at 15:50. Glen Aspinall took off L1 to L3 at 15:55. Tags and notices off.
Re-energised at |  |  |  | 16:00 way 4, 16:05 way 6, by Glen Aspinall.
Tested by |  |  |  | Callum Whittle: live tests after energising passed. Fans run, checked by Kieran Tunnicliffe.
Notes |  |  |  | Certificate EIC-0423 in the job file. Screen at the main switchboard down at 16:15.
Sign-off |  |  |  |  | Name | [6 empty] | Signature | [6 empty] | Date |  |  | Time
Extended: new end time |  |  |  |  | Not extended
Cancelled: area checked |  |  |  |  | Glen Aspinall | [6 empty] | signed | [6 empty] | 26/10/26 |  |  | 15:48
Handed back: area returned |  |  |  |  | Glen Aspinall | [6 empty] | signed | [6 empty] | 26/10/26 |  |  | 16:20
Worked example of a made-up job. Not a permit. · Page 2 of 2