Hot Work Permit Hollins & Reed Contracting Ltd

| Permit no. HR-0417 | Site Unit 3, Canal Side Business Park | Exact location Flat roof over the offices, north end |
| --- | --- | --- |

| Details |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contractor | Hollins & Reed | Issued to | Priya Shah | Valid from | 12/10/26 08:00 |
| Valid to | 12/10/26 17:00 | RAMS ref | HR-RAMS-07 | Fire risk ref | HR-FRA-03 |

| The work |  |
| --- | --- |
| Hot work to be done | Torch-on felt cap sheet to 30 m² of flat roof, with parapet upstands and two outlets. |
| Method | One torch, one cylinder. Laps rolled. Upstands on low flame, gaps behind sealed first. |
| Why cold methods fail | Cold-applied sheet and a heat gun failed a test patch on 9 October. Neither bonded. |

| Hazards |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Combustibles in 10 m | ☒ | Openings and voids | ☒ | Flammables nearby | ☒ | Dust or lint | ☐ |
| Roof or wall linings | ☒ | Below, behind walls | ☒ | Sprinklers, alarms | ☒ | Occupied building | ☒ |

| Precautions | Done | By |
| --- | --- | --- |
| Combustibles removed or covered | ☒ | Priya Shah |
| Floors swept, combustible floors covered | ☒ | Priya Shah |
| Openings and voids sealed | ☒ | Priya Shah |
| Non-combustible screens up | ☐ | Not needed. Open roof |
| Detectors isolated: who restores them | ☒ | Dan Hollins, zone 3 only |
| Gas cylinders secured and checked | ☒ | Priya Shah |
| Two extinguishers within reach: type | ☒ | Two 9 kg dry powder |
| Fire watcher named, breaks covered | ☒ | Reece Ollerton |
| How to raise the alarm | ☒ | Break glass, ring 999 |
| Hot work ends 2 hours before day end | ☒ |  |
| Others shielded from arc and sparks | ☐ | Not needed. No arc |
| Fume: LEV or RPE | ☐ | Not needed. Outdoors |
| Permit shown at the work | ☒ |  |

| Equipment |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Extinguishers | ☒ | Fire blanket | ☒ | Hose reel | ☐ | Gas detector | ☐ |
| Thermal camera | ☒ | Welding screens | ☐ |  | ☐ |  | ☐ |

Other conditions

Cylinder on a heat-insulating base, 3 m from the torch. Never use water on a bitumen fire.

Zone 3 goes back on for any break and when hot work ends. Client told first. Site office 0161 496 0142.

| Sign-off | Name | Signature | Date | Time |
| --- | --- | --- | --- | --- |
| Issued: precautions checked | Dan Hollins | signed | 12/10/26 | 07:50 |
| Accepted: permit understood | Priya Shah | signed | 12/10/26 | 07:55 |

Hot Work Permit Hollins & Reed Contracting Ltd

| Permit no. HR-0417 | Site Unit 3, Canal Side Business Park | Exact location Flat roof over the offices, north end |
| --- | --- | --- |

| Fire watch: continuous for 1 hour, then a check at 2 hours |  |  |  |
| --- | --- | --- | --- |
| When | Time | By | Result |
| During breaks | 12:15 to 12:45 | Reece Ollerton | Torch off for the break. Watched roof and void. Nothing found. |
| End of hot work | 14:45 | Reece Ollerton | Torch off, cylinder shut. Continuous watch started. |
| 1 hour after the end | 15:45 | Reece Ollerton | Watched roof and void the whole hour. Thermal image shows no hot spots. |
| 2 hours after the end | 16:45 | Dan Hollins | Roof and roof void checked. Nothing found. |

| Cancellation |  |
| --- | --- |
| Work stopped at | 14:45 on 12 October. Cap sheet finished. |
| Area checked, images kept | Roof and roof void walked at 16:45. Three thermal images in the job file. |
| Detectors restored by | Dan Hollins. Back on 12:15, off again 12:45, back on 14:50. Panel normal. |
| Equipment removed | Torch, hose and cylinder off the roof by 15:20. |

| Handback |  |
| --- | --- |
| Area returned to | Thornley Vale Estates Ltd, site keyholder |
| Notes | Outlets open again. Nothing to report. |

| Sign-off | Name | Signature | Date | Time |
| --- | --- | --- | --- | --- |
| Extended: new end time | Not extended |  |  |  |
| Cancelled: area checked | Dan Hollins | signed | 12/10/26 | 16:50 |
| Handed back: area returned | Dan Hollins | signed | 12/10/26 | 16:55 |