	Hot Work Permit
Hollins & Reed Contracting Ltd



	Permit no.
HR-0418
	Site
Unit 3, Canal Side Business Park
	Exact location
Basement, beam at grid line C4



	Details
	
	
	
	
	

	Contractor
	Hollins & Reed
	Issued to
	Priya Shah
	Valid from
	13/10/26 08:00

	Valid to
	13/10/26 17:00
	RAMS ref
	HR-RAMS-08
	Fire risk ref
	HR-FRA-03



	The work
	

	Hot work to be done
	Weld two stiffener plates to the existing steel beam, to the engineer’s drawing S-04.

	Method
	Old bracket ground off. MIG welding with argon-mix gas. One welder, one fire watcher.

	Why cold methods fail
	The drawing calls for welded plates. Bolts need holes the flange cannot take.



	Hazards
	
	
	
	
	
	
	

	Combustibles in 10 m
	☒
	Openings and voids
	☒
	Flammables nearby
	☐
	Dust or lint
	☐

	Roof or wall linings
	☐
	Below, behind walls
	☒
	Sprinklers, alarms
	☒
	Occupied building
	☒



	Precautions
	Done
	By

	Combustibles removed or covered
	☒
	Reece Ollerton

	Floors swept, combustible floors covered
	☒
	Reece Ollerton

	Openings and voids sealed
	☒
	Reece Ollerton

	Non-combustible screens up
	☒
	Reece Ollerton

	Detectors isolated: who restores them
	☒
	Dan Hollins, zone 1 only

	Gas cylinders secured and checked
	☒
	Priya Shah

	Two extinguishers within reach: type
	☒
	CO2 and dry powder

	Fire watcher named, breaks covered
	☒
	Reece Ollerton

	How to raise the alarm
	☒
	Break glass, ring 999

	Hot work ends 2 hours before day end
	☒
	

	Others shielded from arc and sparks
	☒
	Priya Shah, screens

	Fume: LEV or RPE
	☒
	LEV and RPE, both

	Permit shown at the work
	☒
	



	Equipment
	
	
	
	
	
	
	

	Extinguishers
	☒
	Fire blanket
	☒
	Hose reel
	☐
	Gas detector
	☐

	Thermal camera
	☒
	Welding screens
	☒
	
	☐
	
	☐



	Other conditions

	No flammable gas below ground. Extraction at the weld, ducted outside. Welder wears RPE as well.

	Riser boarded. Watcher checks the office above and behind the riser wall. Site office 0161 496 0142.



	Sign-off
	Name
	Signature
	Date
	Time

	Issued: precautions checked
	Dan Hollins
	signed
	13/10/26
	07:50

	Accepted: permit understood
	Priya Shah
	signed
	13/10/26
	07:55
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	Fire watch: continuous for 1 hour, then a check at 2 hours

	When
	Time
	By
	Result

	During breaks
	12:00 to 12:30
	Reece Ollerton
	Stopped for the break. Watched basement and riser. Nothing found.

	End of hot work
	14:30
	Reece Ollerton
	Welding finished. Continuous watch started.

	1 hour after the end
	15:30
	Reece Ollerton
	Watch kept the whole hour. Office above and riser checked.

	2 hours after the end
	16:30
	Dan Hollins
	Basement, riser and office above checked. Nothing found.

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	



	Cancellation
	

	Work stopped at
	14:30 on 13 October. Plates welded.

	Area checked, images kept
	Walked at 16:30. Two thermal images of the riser in the job file.

	Detectors restored by
	Dan Hollins. Back on 12:00, off again 12:30, back on 14:35. Panel normal.

	Equipment removed
	Welder, cylinder and screens out by 15:00. Riser boards stay.



	Handback
	

	Area returned to
	Dan Hollins, for the next trade

	Notes
	Welds to be inspected by the engineer. Not part of this permit.



	Sign-off
	Name
	Signature
	Date
	Time

	Extended: new end time
	Not extended
	
	
	

	Cancelled: area checked
	Dan Hollins
	signed
	13/10/26
	16:35

	Handed back: area returned
	Dan Hollins
	signed
	13/10/26
	16:40
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