Hot Work Permit Hollins & Reed Contracting Ltd

| Permit no. HR-0418 | Site Unit 3, Canal Side Business Park | Exact location Basement, beam at grid line C4 |
| --- | --- | --- |

| Details |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contractor | Hollins & Reed | Issued to | Priya Shah | Valid from | 13/10/26 08:00 |
| Valid to | 13/10/26 17:00 | RAMS ref | HR-RAMS-08 | Fire risk ref | HR-FRA-03 |

| The work |  |
| --- | --- |
| Hot work to be done | Weld two stiffener plates to the existing steel beam, to the engineer’s drawing S-04. |
| Method | Old bracket ground off. MIG welding with argon-mix gas. One welder, one fire watcher. |
| Why cold methods fail | The drawing calls for welded plates. Bolts need holes the flange cannot take. |

| Hazards |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Combustibles in 10 m | ☒ | Openings and voids | ☒ | Flammables nearby | ☐ | Dust or lint | ☐ |
| Roof or wall linings | ☐ | Below, behind walls | ☒ | Sprinklers, alarms | ☒ | Occupied building | ☒ |

| Precautions | Done | By |
| --- | --- | --- |
| Combustibles removed or covered | ☒ | Reece Ollerton |
| Floors swept, combustible floors covered | ☒ | Reece Ollerton |
| Openings and voids sealed | ☒ | Reece Ollerton |
| Non-combustible screens up | ☒ | Reece Ollerton |
| Detectors isolated: who restores them | ☒ | Dan Hollins, zone 1 only |
| Gas cylinders secured and checked | ☒ | Priya Shah |
| Two extinguishers within reach: type | ☒ | CO2 and dry powder |
| Fire watcher named, breaks covered | ☒ | Reece Ollerton |
| How to raise the alarm | ☒ | Break glass, ring 999 |
| Hot work ends 2 hours before day end | ☒ |  |
| Others shielded from arc and sparks | ☒ | Priya Shah, screens |
| Fume: LEV or RPE | ☒ | LEV and RPE, both |
| Permit shown at the work | ☒ |  |

| Equipment |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Extinguishers | ☒ | Fire blanket | ☒ | Hose reel | ☐ | Gas detector | ☐ |
| Thermal camera | ☒ | Welding screens | ☒ |  | ☐ |  | ☐ |

Other conditions

No flammable gas below ground. Extraction at the weld, ducted outside. Welder wears RPE as well.

Riser boarded. Watcher checks the office above and behind the riser wall. Site office 0161 496 0142.

| Sign-off | Name | Signature | Date | Time |
| --- | --- | --- | --- | --- |
| Issued: precautions checked | Dan Hollins | signed | 13/10/26 | 07:50 |
| Accepted: permit understood | Priya Shah | signed | 13/10/26 | 07:55 |

Hot Work Permit Hollins & Reed Contracting Ltd

| Permit no. HR-0418 | Site Unit 3, Canal Side Business Park | Exact location Basement, beam at grid line C4 |
| --- | --- | --- |

| Fire watch: continuous for 1 hour, then a check at 2 hours |  |  |  |
| --- | --- | --- | --- |
| When | Time | By | Result |
| During breaks | 12:00 to 12:30 | Reece Ollerton | Stopped for the break. Watched basement and riser. Nothing found. |
| End of hot work | 14:30 | Reece Ollerton | Welding finished. Continuous watch started. |
| 1 hour after the end | 15:30 | Reece Ollerton | Watch kept the whole hour. Office above and riser checked. |
| 2 hours after the end | 16:30 | Dan Hollins | Basement, riser and office above checked. Nothing found. |

| Cancellation |  |
| --- | --- |
| Work stopped at | 14:30 on 13 October. Plates welded. |
| Area checked, images kept | Walked at 16:30. Two thermal images of the riser in the job file. |
| Detectors restored by | Dan Hollins. Back on 12:00, off again 12:30, back on 14:35. Panel normal. |
| Equipment removed | Welder, cylinder and screens out by 15:00. Riser boards stay. |

| Handback |  |
| --- | --- |
| Area returned to | Dan Hollins, for the next trade |
| Notes | Welds to be inspected by the engineer. Not part of this permit. |

| Sign-off | Name | Signature | Date | Time |
| --- | --- | --- | --- | --- |
| Extended: new end time | Not extended |  |  |  |
| Cancelled: area checked | Dan Hollins | signed | 13/10/26 | 16:35 |
| Handed back: area returned | Dan Hollins | signed | 13/10/26 | 16:40 |