## Hot Work Permit
Hot Work Permit
Hollins & Reed Contracting Ltd
Permit no. |  | Site | [8 empty] | Exact location
HR-0418 |  | Unit 3, Canal Side Business Park | [8 empty] | Basement, beam at grid line C4
Details
Contractor | Hollins & Reed |  |  |  |  | Issued to |  |  | Priya Shah |  |  |  |  | Valid from |  |  |  |  | 13/10/26 08:00
Valid to | 13/10/26 17:00 |  |  |  |  | RAMS ref |  |  | HR-RAMS-08 |  |  |  |  | Fire risk ref |  |  |  |  | HR-FRA-03
The work
Hot work to be done |  |  | Weld two stiffener plates to the existing steel beam, to the engineer’s drawing S-04.
Method |  |  | Old bracket ground off. MIG welding with argon-mix gas. One welder, one fire watcher.
Why cold methods fail |  |  | The drawing calls for welded plates. Bolts need holes the flange cannot take.
Hazards
Combustibles in 10 m |  | ☒ | Openings and voids |  |  |  |  | ☒ |  | Flammables nearby |  |  |  |  | ☐ | Dust or lint |  |  |  |  | ☐
Roof or wall linings |  | ☐ | Below, behind walls |  |  |  |  | ☒ |  | Sprinklers, alarms |  |  |  |  | ☒ | Occupied building |  |  |  |  | ☒
Precautions | [12 empty] | Done |  |  |  | By
Combustibles removed or covered | [12 empty] | ☒ |  |  |  | Reece Ollerton
Floors swept, combustible floors covered | [12 empty] | ☒ |  |  |  | Reece Ollerton
Openings and voids sealed | [12 empty] | ☒ |  |  |  | Reece Ollerton
Non-combustible screens up | [12 empty] | ☒ |  |  |  | Reece Ollerton
Detectors isolated: who restores them | [12 empty] | ☒ |  |  |  | Dan Hollins, zone 1 only
Gas cylinders secured and checked | [12 empty] | ☒ |  |  |  | Priya Shah
Two extinguishers within reach: type | [12 empty] | ☒ |  |  |  | CO2 and dry powder
Fire watcher named, breaks covered | [12 empty] | ☒ |  |  |  | Reece Ollerton
How to raise the alarm | [12 empty] | ☒ |  |  |  | Break glass, ring 999
Hot work ends 2 hours before day end | [12 empty] | ☒
Others shielded from arc and sparks | [12 empty] | ☒ |  |  |  | Priya Shah, screens
Fume: LEV or RPE | [12 empty] | ☒ |  |  |  | LEV and RPE, both
Permit shown at the work | [12 empty] | ☒
Equipment
Extinguishers |  | ☒ | Fire blanket |  |  |  |  | ☒ |  | Hose reel |  |  |  |  | ☐ | Gas detector |  |  |  |  | ☐
Thermal camera |  | ☒ | Welding screens |  |  |  |  | ☒ | [6 empty] | ☐ | [5 empty] | ☐
Other conditions
No flammable gas below ground. Extraction at the weld, ducted outside. Welder wears RPE as well.
Riser boarded. Watcher checks the office above and behind the riser wall. Site office 0161 496 0142.
Sign-off |  |  |  |  | Name | [5 empty] | Signature | [6 empty] | Date |  | Time
Issued: precautions checked |  |  |  |  | Dan Hollins | [5 empty] | signed | [6 empty] | 13/10/26 |  | 07:50
Accepted: permit understood |  |  |  |  | Priya Shah | [5 empty] | signed | [6 empty] | 13/10/26 |  | 07:55
Worked example of a made-up job. Not a permit. · Page 1 of 2
Hot Work Permit
Hollins & Reed Contracting Ltd
Permit no. |  | Site | [8 empty] | Exact location
HR-0418 |  | Unit 3, Canal Side Business Park | [8 empty] | Basement, beam at grid line C4
Fire watch: continuous for 1 hour, then a check at 2 hours
When |  |  |  | Time |  |  | By |  |  |  |  | Result
During breaks |  |  |  | 12:00 to 12:30 |  |  | Reece Ollerton |  |  |  |  | Stopped for the break. Watched basement and riser. Nothing found.
End of hot work |  |  |  | 14:30 |  |  | Reece Ollerton |  |  |  |  | Welding finished. Continuous watch started.
1 hour after the end |  |  |  | 15:30 |  |  | Reece Ollerton |  |  |  |  | Watch kept the whole hour. Office above and riser checked.
2 hours after the end |  |  |  | 16:30 |  |  | Dan Hollins |  |  |  |  | Basement, riser and office above checked. Nothing found.
Cancellation
Work stopped at |  |  | 14:30 on 13 October. Plates welded.
Area checked, images kept |  |  | Walked at 16:30. Two thermal images of the riser in the job file.
Detectors restored by |  |  | Dan Hollins. Back on 12:00, off again 12:30, back on 14:35. Panel normal.
Equipment removed |  |  | Welder, cylinder and screens out by 15:00. Riser boards stay.
Handback
Area returned to |  |  | Dan Hollins, for the next trade
Notes |  |  | Welds to be inspected by the engineer. Not part of this permit.
Sign-off |  |  |  |  | Name | [5 empty] | Signature | [6 empty] | Date |  | Time
Extended: new end time |  |  |  |  | Not extended
Cancelled: area checked |  |  |  |  | Dan Hollins | [5 empty] | signed | [6 empty] | 13/10/26 |  | 16:35
Handed back: area returned |  |  |  |  | Dan Hollins | [5 empty] | signed | [6 empty] | 13/10/26 |  | 16:40
Worked example of a made-up job. Not a permit. · Page 2 of 2