	Permit to Dig
Hollins & Reed Contracting Ltd



	Permit no.
HR-0419
	Site
Unit 3, Canal Side Business Park
	Exact location
East yard, gully to manhole MH2



	Details
	
	
	
	
	

	Contractor
	Hollins & Reed
	Issued to
	Priya Shah
	Valid from
	14/10/26 08:00

	Valid to
	14/10/26 16:30
	RAMS ref
	HR-RAMS-09
	Drawing, date
	HR-D-02, 05/10/26



	The work
	

	Where, depth, method
	Trench 6 m long, 1.2 m deep. Breaker through concrete, then mini excavator with a spotter.

	Hand dig zone
	Hand tools only near marked lines. Breaker 500 mm off them. Insulated tools by the cable.



	Hazards
	
	
	
	
	
	
	

	Electricity
	☒
	Gas
	☒
	Water
	☒
	Telecoms
	☐

	Drains and sewers
	☒
	District heating
	☐
	Contaminated ground
	☐
	Unstable ground
	☒

	Water ingress
	☒
	Traffic
	☒
	Services unknown
	☐
	
	☐



	Precautions
	Done
	By

	Drawings obtained and dated
	☒
	Dan Hollins, 05/10/26

	Scanned with locator and signal generator
	☒
	Dan Hollins, 13/10/26

	Services marked on the plan and ground
	☒
	Dan Hollins

	Trial holes hand dug
	☒
	Priya Shah, two holes

	Services exposed and supported
	☐
	Not needed. None crossed

	Edge protection and ladders in place
	☒
	Reece Ollerton

	Spoil kept back from the edge
	☒
	Reece Ollerton

	Sides supported or battered
	☒
	Priya Shah, supports

	Inspected at the start of each shift
	☒
	Dan Hollins

	Gas monitoring, traffic management
	☒
	Reece Ollerton, barriers



	Services made dead
	How
	Locked
	Tag
	Proved by

	Nothing isolated
	All services stay live
	☐
	
	



	People on this permit: name
	Company
	Briefed

	Priya Shah
	Hollins & Reed
	☒

	Reece Ollerton
	Hollins & Reed
	☒



	Other conditions

	Treat every service as live. Re-scan as the trench deepens. Unknown service, stop and ring 0161 496 0142.

	Cable struck, driver stays in the cab. Nobody goes near until the owner makes it safe.



	Sign-off
	Name
	Signature
	Date
	Time

	Issued: precautions checked
	Dan Hollins
	signed
	14/10/26
	07:45

	Accepted: permit understood
	Priya Shah
	signed
	14/10/26
	07:50
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	Excavation inspections

	Date
	Time
	By
	Result

	14/10/26
	13:00
	Dan Hollins
	Trench at 0.9 m. Supports in, sides sound, barriers up.

	15/10/26
	07:45
	Dan Hollins
	Start of shift, after rain. Pumped out. Sides sound.

	15/10/26
	12:45
	Dan Hollins
	Before backfilling. Sides, supports and barriers sound.

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	



	Cancellation
	

	Backfilled or secured
	Backfilled in layers. Concrete reinstated 15 October. No concrete around services.

	Services as found
	Cable and gas pipe where the drawing shows. Neither touched.

	Drawings marked up
	New drain added to HR-D-02. Copy to the site plan.



	Handback
	

	Isolations removed
	None were made

	Area returned to
	Thornley Vale Estates Ltd, site keyholder

	Notes
	Yard open again. Barriers gone.



	Sign-off
	Name
	Signature
	Date
	Time

	Extended: new end time
	Dan Hollins, to 15/10 16:00
	signed
	14/10/26
	16:15

	Cancelled: area checked
	Dan Hollins
	signed
	15/10/26
	15:30

	Handed back: area returned
	Dan Hollins
	signed
	15/10/26
	15:40
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